## 신규 양식 및 data
No | Product type | Regulation category | Region | Country | Detail | Checking data | Image | File | Evidence | Result | Remark
A-16-1 | common | common | common | common | Instructions to use inert gas when detecting refrigerant leaks or when cleaning or repairing pipes. (It may cause explosion) - 1 | Inert gas (oxygen free nitrogen) should be used when you checking for leaks, cleaning or repairs of pipes etc. If you are using combustible gases including oxygen, appliance may have the risk of fires and explosions.
A-16-2 | common | common | common | common | Instructions to use inert gas when detecting refrigerant leaks or when cleaning or repairing pipes. (It may cause explosion) - 2 | Prior to recharging the system it shall be pressure tested with oxygen free nitrogen (OFN).
A-16-3 | common | common | common | common | Instructions to use inert gas when detecting refrigerant leaks or when cleaning or repairing pipes. (It may cause explosion) - 3 | Oxygen free nitrogen (OFN) shall be purged through the system both before and during the brazing process.
A-17 | common | common | common | common | Precautions when removing air through valves or pipes. | Use non-flammable gas (nitrogen) to CHECK for leak and to purge air.
A-19-1 | common | common | common | common | Information on the space required when installing the product. (Left and Right of indoor unit) | Maintain a clearance of at least 10 cm from the right and left sides of the indoor unit.
A-19-2 | common | common | common | common | Information on the space required when installing the product. (Top of indoor unit) | Maintain a clearance of at least 12 cm between the top of the indoor unit and the ceiling.
A-19-3 | common | common | common | common | Information on the space required when installing the product. (Height of indoor unit) | Maintain a clearance of at least 180 cm between the bottom of the indoor unit and the floor.
A-19-4 | common | common | common | common | Information on the space required when installing the product. (outdoor unit for each side) | Maintain a clearance of 30 cm from the left and the back(air inlet) sides and 60 cm from the right sides of the outdoor unit.
A-19-5 | common | common | common | common | Information on the space required when installing the product. (outdoor unit for obstacle) | If there is an obstacle in front of the air vent, keep the outdoor unit at a distance of at least 70 cm from the obstacle.
A-22 | common | common | common | common | Do not operate the product or turn on the power of the product while the cover with wires or electrical devices is open. | Do not turn on the breaker or power under condition that front panel, cabinet, top cover, control box cover are removed or opened. Otherwise, it may cause fire, electric shock, explosion or death.
A-32 | common | common | common | common | Precautions for special installation (heavy snowy areas, strong windy areas, extremely cold or humid areas) | Precautions for Installation in Special Regions (Snowfall, Strong Winds, Area with Severely Cold or Humid Weather)
A-45 | common | common | common | common | Instructions for cleaning the inside of the product. | To clean the interior, contact an authorized service center or dealer. Using harsh detergents may cause corrosion or damage to the unit.
A-56-1 | common | common | common | common | Is open source licence content added up in the manual? -1 | To obtain the source code that is contained in this product, under GPL, LGPL, MPL, and other open source licenses that have the obligation to disclose source code, and to access all referred license terms, copyright notices and other relevant documents, please visit https://opensource.lge.com.
A-56-2 | common | common | common | common | Is open source licence content added up in the manual? -2 | LG Electronics will also provide open source code to you on CD-ROM for a charge covering the cost of performing such distribution (such as the cost of media, shipping, and handling) upon email request to opensource@lge.com. This offer is valid to anyone in receipt of this information for a period of three years after our last shipment of this product.
A-56-3 | common | common | common | common | Is open source licence content added up in the manual? -3 | This offer is valid to anyone in receipt of this information for a period of three years after our last shipment of this product.
A-62 | common | common | common | common | Added a Note sentence in the Auto change over function of wall-mounted air conditioners for Indian products - Minimum cooling temperature is limited to 24℃ | Default temperature will be minimum 24℃(in cooling mode), when operated with remote control except power failure/power switched off.
A-64 | common | common | common | common | Have sentences been added to the content of doing Smart Diagnosis? | - For reasons not attributable to LGE’s negligence, the service may not operate due to external factors such as, but not limited to, Wi-Fi unavailability, Wi-Fi disconnection, local app store policy, or app unavailability. - The feature may be subject to change without prior notice and may have a different form depending on where you are located.
J-142 | common | common | common | common | If UV-C is attached to the product, is the caution statement reflected so that users do not stare at UV-C? | This appliance contains a UV emitter. Do not stare at the light source.
J-144 | common | common | common | common | Is there a guideline instructing infants or users with physical or mental disabilities to be careful not to cause problems while using the product? | This appliance can be used by children aged from 8 years and above and persons with reduced physical, sensory or mental capabilities or lack of experience and knowledge if they have been given supervision or instruction concerning use of the appliance in a safe way and understand the hazards involved. Children shall not play with the appliance. Cleaning and user maintenance shall not be made by children without supervision.
C-9 | common | common | common | common | Is there a warning that the product must always be grounded? | Always ground the product -1 - There is risk of fire or electric shock
C-9-1 | common | common | common | common | Is there a warning that the product must always be grounded? | Always ground the product -2 - There is risk of fire or electric shock
C-9-2 | common | common | common | common | Is there a warning that the product must always be grounded? | Always ground the product -3 - There is risk of fire or electric shock
C-10 | common | common | common | common | Are there instructions to always install the product through a salesperson or a professional service center? | For installation, always contact the dealer or an Authorized Service Center. - There is risk of fire, electric shock, explosion or injury.
C-11-1 | common | common | common | common | Are there warnings to be careful not to disconnect or break the product cable? | Take care to ensure that power cable could not be pulled out or damaged during operation. - There is risk of fire or electric shock.
C-11-2 | common | common | common | common | Are there warnings to be careful not to disconnect or break the product cable? | Take care to ensure that power cable could not be pulled out or damaged during operation. - There is risk of fire or electric shock.
C-12-1 | common | common | common | common | When installing the product, is there a notice saying that the wires are properly connected? - 1 | Make the connection securely so that sccrew in terminals may not be loosed when pulling cable.
C-12-2 | common | common | common | common | When installing the product, is there a notice saying that the wires are properly connected? - 2 | Make the connection securely so that sccrew in terminals may not be loosed when pulling cable.
C-13 | common | common | common | common | Is there a cautionary statement not to touch piping or internal parts while the product is operating or starting operation? | Do not touch refrigerant pipe and water pipe or any internal parts while the unit is operating or immediately after operation. - There is risk of burns or frostbite, personal injury.
C-14-1 | common | common | common | common | When installing the product, is there a guide sentence to install it horizontally? - 1 | Keep level parallel in installing the product. Otherwise, it may cause vibration or water leakage.
C-14-2 | common | common | common | common | When installing the product, is there a guide sentence to install it horizontally? - 2 | Keep level parallel in installing the product. Otherwise, it may cause vibration or water leakage.
C-15-1 | common | common | common | common | Is there a notice that the installation location of the product must be determined so as not to cause damage to outside pedestrians or neighbors? | Install the product so that the noise or hot wind from the outdoor unit may not cause any damage to the neighbors. - Otherwise, it may cause dispute with the neighbors.
C-15-2 | common | common | common | common | Is there a notice that the installation location of the product must be determined so as not to cause damage to outside pedestrians or neighbors? | Install the product so that the noise or hot wind from the outdoor unit may not cause any damage to the neighbors. - Otherwise, it may cause dispute with the neighbors.
C-16 | common | common | common | common | Is there a notice saying that leakage should be checked after installing the product? | Always inspect gas leakage after the installation and repair of product. - Otherwise, it may cause the failure of product.
C-17 | common | common | common | common | Is there a warning not to use different types or mixed types of batteries when replacing batteries in the product or in the remote control? | Replace the all batteries in the remote control with new ones of the same type. Do not mix old and new batteries or different types of batteries. - There is risk of fire or explosion.
C-18-1 | common | common | common | common | Are you guiding young children not to climb on the product? | Take care so that children may not step on the outdoor unit. - Otherwise, children may be seriously injured due to falling down.
C-18-2 | common | common | common | common | Are you guiding young children not to climb on the product? | Take care so that children may not step on the outdoor unit. - Otherwise, children may be seriously injured due to falling down.
C-19 | common | common | common | common | Are there instructions not to place objects on the product? | Do not step on the indoor/outdoor unit and do not put anything on it.
J-1 | common | common | common | common | Is there guidance on installation space for products using flammable refrigerants? | The appliance shall be stored in a well-ventilated area where the room size corresponds to the room area as specified for operation
J-2 | common | common | common | common | Is there guidance on the installation location of products using flammable refrigerants? (1) | The appliance shall be stored in a room without continuously operating open flames (for example an operating gas appliance) and ignition sources (for example an operating electric heater).
J-3 | common | common | common | common | Are there any precautions for damage to products using flammable refrigerants? | The appliance shall be stored so as to prevent mechanical damage from occurring.
J-4 | common | common | common | common | Is there guidance on refrigerant compatibility? | Compliance with national gas regulations shall be observed.
J-5 | common | common | common | common | Are there any precautions for air conditioner connection piping? (1) | Refrigerant tubing shall be protected or enclosed to avoid damage.
J-6 | common | common | common | common | Are there any precautions for air conditioner connection piping? (2) | Flexible refrigerant connectors (such as connecting lines between the indoor and outdoor unit) that may be displaced during normal operations shall be protected against mechanical damage.
J-7 | common | common | common | common | Is there guidance on the length of pipe installation? | The installation of pipe-work shall be kept to a minimum.
J-8 | common | common | common | common | Are there any precautions regarding the order of welding work when installing or repairing air conditioners? | A brazed, welded, or mechanical connection shall be made before opening the valves to permit refrigerant to flow between the refrigerating system parts.
J-9 | common | common | common | common | Is there guidance on repair and installation qualifications for products using flammable refrigerants? (1) | Any person who is involved with working on or breaking into a refrigerant circuit should hold a current valid certificate from an industry-accredited assessment authority, which authorises their competence to handle refrigerants safely in accordance with an industry recognised assessment specification.
J-10 | common | common | common | common | Is there guidance on repair and installation qualifications for products using flammable refrigerants? (2) | Servicing shall only be performed as recommended by the equipment manufacturer. Maintenance and repair requiring the assistance of other skilled personnel shall be carried out under the supervision of the person competent in the use of flammable refrigerants.
J-11 | common | common | common | common | Are there any precautions for product cleaning? | Do not use means to accelerate the defrosting process or to clean, other than those recommended by the manufacturer.
J-11 | common | common | common | common | Is there guidance on the installation location of products using flammable refrigerants? (2) | The appliance shall be stored in a room without continuously operating ignition sources (for example: open flames, an operating gas appliance or an operating electric heater.)
J-11 | common | common | common | common | Guidance on n'ot damaging the product' | Do not pierce or burn.
J-11 | common | common | common | common | Precautions for handling refrigerants | Be aware that refrigerants may not contain an odour.
J-13 | common | common | common | common | Precautions for installation ventilation of products using flammable refrigerants | Keep any required ventilation openings clear of obstruction.
J-15 | common | common | common | common | If a product using a flammable refrigerant is the contents of the product installation area? | Prior to beginning work on systems containing flammable refrigerants, safety checks are necessary to ensure that the risk of ignition is minimised. For repair to the refrigerating system, the following precautions shall be complied with prior to conducting work on the system.
J-16 | common | common | common | common | If a product that uses flammable refrigerants is the process of work? | Work shall be undertaken under a controlled procedure so as to minimise the risk of a flammable gas or vapour being present while the work is being performed.
J-17 | common | common | common | common | If a product that uses flammable refrigerants is there a check on the product installation environment? | All maintenance staff and others working in the local area shall be instructed on the nature of work being carried out. Work in confined spaces shall be avoided.
J-18 | common | common | common | common | If a product using a flammable refrigerant is there a check on the leakage of the refrigerant? | The area shall be checked with an appropriate refrigerant detector prior to and during work, to ensure the technician is aware of potentially flammable atmospheres. Ensure that the leak detection equipment being used is suitable for use with flammable refrigerants, i.e. non-sparking, adequately sealed or intrinsically safe.
J-19 | common | common | common | common | If a product that uses flammable refrigerants is the preparation of fire extinguisher equipment? | If any hot work is to be conducted on the refrigerating equipment or any associated parts, appropriate fire extinguishing equipment shall be available to hand. Have a dry powder or CO2 fire extinguisher adjacent to the charging area.
J-20 | common | common | common | common | If a product that uses a flammable refrigerant is there for the removal of the ignition source? | No person carrying out work in relation to a refrigerating system which involves exposing any pipe work that contains or has contained flammable refrigerant shall use any sources of ignition in such a manner that it may lead to the risk of fire or explosion. All possible ignition sources, including cigarette smoking, should be kept sufficiently far away from the site of installation, repairing, removing and disposal, during which flammable refrigerant can possibly be released to the surrounding space. Prior to work taking place, the area around the equipment is to be surveyed to make sure that there are no flammable hazards or ignition risks. “No Smoking” signs shall be displayed.
J-21 | common | common | common | common | In the case of products using flammable refrigerants, is there an air vent for the installation environment? | Ensure that the area is in the open or that it is adequately ventilated before breaking into the system or conducting any hot work. A degree of ventilation shall continue during the period that the work is carried out. The ventilation should safely disperse any released refrigerant and preferably expel it externally into the atmosphere.
J-22-1 | common | common | common | common | Do you have any instructions on the replacement of equipment for products using flammable refrigerants? - 1 | Where electrical components are being changed, they shall be fit for the purpose and to the correct specification. At all times the manufacturer’s maintenance and service guidelines shall be followed. If in doubt consult the manufacturer’s technical department for assistance. The following checks shall be applied to installations using flammable refrigerants:
J-22-2 | common | common | common | common | Do you have any instructions on the replacement of equipment for products using flammable refrigerants? - 2 | the actual refrigerant charge is in accordance with the room size within which the refrigerant containing parts are installed
J-22-3 | common | common | common | common | Do you have any instructions on the replacement of equipment for products using flammable refrigerants? - 3 | the ventilation machinery and outlets are operating adequately and are not obstructed
J-22-4 | common | common | common | common | Do you have any instructions on the replacement of equipment for products using flammable refrigerants? - 4 | if an indirect refrigerating circuit is being used, the secondary circuit shall be checked for the presence of refrigerant
J-22-5 | common | common | common | common | Do you have any instructions on the replacement of equipment for products using flammable refrigerants? - 5 | marking to the equipment continues to be visible and legible. Markings and signs that are illegible shall be corrected
J-22-6 | common | common | common | common | Do you have any instructions on the replacement of equipment for products using flammable refrigerants? - 6 | refrigerating pipe or components are installed in a position where they are unlikely to be exposed to any substance which may corrode refrigerant containing components, unless the components are constructed of materials which are inherently resistant to being corroded or are suitably protected against being so corroded.
J-23-1 | common | common | common | common | If a product using a flammable refrigerant is the contents of repair and maintenance for electrical parts? - 1 | Repair and maintenance to electrical components shall include initial safety checks and component inspection procedures. If a fault exists that could compromise safety, then no electrical supply shall be connected to the circuit until it is satisfactorily dealt with. If the fault cannot be corrected immediately but it is necessary to continue operation, an adequate temporary solution shall be used. This shall be reported to the owner of the equipment so all parties are advised. Initial safety checks shall include:
J-23-2 | common | common | common | common | If a product using a flammable refrigerant is the contents of repair and maintenance for electrical parts? - 2 | Capacitors are discharged: this shall be done in a safe manner to avoid possibility of sparking.
J-23-3 | common | common | common | common | If a product using a flammable refrigerant is the contents of repair and maintenance for electrical parts? - 3 | No live electrical components and wiring are exposed while charging, recovering or purging the system.
J-23-4 | common | common | common | common | If a product using a flammable refrigerant is the contents of repair and maintenance for electrical parts? - 4 | Continuity of earth bonding
J-34 | common | common | common | common | If you are subject to PED (European pressure vessel certification), are there any instructions on piping connections? | Copper in contact with refrigerants shall be oxygen-free or de-oxidized
J-35 | common | common | common | common | In the case of PED (European pressure vessel certification), the appearance of the pipe is less than 20mm and only Annewaled Pipe should be used. | Temper grade of pipe: Annealed
J-36-1 | common | common | common | common | Do you have any guidance on how to cut the pipe and how to remove the BURR? - 1 | Cut the pipe with a copper tube cutter.
J-36-2 | common | common | common | common | Do you have any guidance on how to cut the pipe and how to remove the BURR? - 2 | Remove the burrs using a reamer.
J-37 | common | common | common | common | If you are subject to PED (European pressure vessel certification), do you have instructions on the use of Torque values ​​and spanner when you tighten the pipe? | After fixing the pipe with the help an adjustable wrench, securely tighten the flare nut using a torque wrench.
J-40 | common | common | common | common | For maintenance, connection pipes or mechanical connection devices should be accessible. | Mechanical connections (mechanical connectors or flared joints) shall be accessible for maintenance purposes
J-41 | common | common | common | common | Piping connections should be prevented from physical damage. | Pipe-work shall be protected from physical damage.
J-42-1 | common | common | common | common | Sealing, finishing should be re -processed when re -connecting piping or mechanical connection devices. - 1 | When mechanical connectors are reused indoors, sealing parts shall be renewed.
J-42-2 | common | common | common | common | Sealing, finishing should be re -processed when re -connecting piping or mechanical connection devices. - 2 | When flared joints are reused indoors, the flare part shall be re-fabricated.
J-54 | common | common | common | common | Do you have any instructions for your physical condition or age when using the product? | This appliance is not intended for use by persons (including children) with reduced physical, sensory or mental capabilities or lack of experience and knowledge, unless they have been given supervision or instruction concerning use of the appliance by a person responsible for their safety. Children should be supervised to ensure that they do not play with the appliance.
J-61-1 | common | common | common | common | The notice that the installation of the product should be installed according to the national wiring rules | The appliance shall be installed in accordance with national wiring regulations.
J-61-2 | common | common | common | common | The notice that the installation of the product should be installed according to the national wiring rules | The appliance shall be installed in accordance with national wiring regulations.
J-66 | common | common | common | common | How to connect the product, how to connect parts | All power wiring/communication cables must comply with applicable local and national codes.
J-112 | common | common | common | common | Notify that it is a product using UV-C LMAP | This appliance contains a UV-C lamp.
J-113 | common | common | common | common | Guide to maintenance guidelines when using UV-C LMAP | Read the maintenance instructions before opening the appliance.
J-114 | common | common | common | common | Products that use UV-C LAMP are cleaning and maintenance of power separation precautions | Before cleaning or performing maintenance, disconnect the power supply and wait until the fan stops.
J-115 | common | common | common | common | Methods, frequency of cleaning, precautions to be taken | the method, frequency of cleaning, and necessary precautions to be taken.
J-116 | common | common | common | common | Prevention measures that can be taken when replacing the UV-C emission and a starter (if corresponding) | precautions to be taken when replacing UV-C emitters and starters, if applicable.
J-117 | common | common | common | common | The use or housing damage of unintended devices can avoid dangerous UV-C radiation. UV-C radiation can harm your eyes and skin even if you take small quantities. | unintended use of the appliance or damage to the housing may result in the escape of dangerous UV-C radiation. UV-C radiation may, even in small doses, cause harm to the eyes and skin.
J-118 | common | common | common | common | Clearly damaged devices should not work. | Appliances that are obviously damaged must not be operated.
J-119 | common | common | common | common | Before replacing the UV-C lamp, the product must be separated from the power supply. | The appliance must be disconnected from. The supply before replacing the UV-C lamp.
J-121 | common | common | common | common | It is a good idea to separate the power before opening the panel that opens and approaches the doors displayed with UV risk symbols to maintain the user. | Before opening doors and access panels bearing the ultraviolet radiation hazard symbol for the conducting user maintenance, it is recommended to disconnect the power.
J-123 | common | common | common | common | For devices with UV-C lamps, information about UV-C lamp replacement, including models and / or component numbers, should be provided. | Model name: LTPL-G35UV275GS-JA, LTPL-G35U275GS-TWA, CUD7GF1A
J-124 | common | common | common | common | When installing on-site, the UV-C sterilization lamp system specified by a factory approved to use with the product should be specified in the instructions with a specific model number. | Model name: LTPL-G35UV275GS-JA, LTPL-G35U275GS-TWA, CUD7GF1A
J-126-1 | common | common | common | common | Information on the explosion risk for installation location | Do not install the unit in potentially explosive atmospheres.
J-126-2 | common | common | common | common | Information on the explosion risk for installation location | Do not install the unit in potentially explosive atmospheres.
J-151 | common | common | common | common | The manual should include specific information about the required qualification of the operator for maintenance, service and repair work. All work procedures that affect safety means should only be performed by jurisdictions according to the accessories HH. | The refrigerant and insulation blowing gas used in the appliance require special disposal procedures. Consult a service agent or a similarly qualified person before disposing of them.
J-173-1 | common | common | common | common | Guide to the service method | Servicing shall be performed only as recommended by the manufacturer.
J-173-2 | common | common | common | common | Guide to the service method | Servicing shall be performed only as recommended by the manufacturer.

## 수정 내용
※ 해당 체크리스트는 LG 시스템 내에서 모델 및 필터링을 통해 제작되는 형식으로 매뉴얼 점검사항 外 타 내용 포함. 매뉴얼 점검사항일 경우에는 필터링을 통해서 Image 란에는 공란 반영
No | Product type | Regulation Category | Region | Country | Detail | Checking data | Image | File | Evidence | Result | Remark
| ※ 기존 반영 | [7 empty] | ※ 수정 반영
| No. | Detail(English) | Detail(Korean) | Type | 표준 문장 | 매뉴얼 반영 문장 |  |  | No | Product type | Regulation Category | Region | Country | Detail | Checking data | Image | File | Evidence | Result | Remark
Checking data = 표준 문장
매뉴얼 점검 항목에는 Image, File 없음
단, Checking data에는 표준 문장
제품군
항목
예시)
- 사내표준
- 안전규격
- 에너지규격
-친환경규제
- 소비자보호규제
등...
지역
- 공통
- 아시아
- 북미
- 유럽
- CIS
등..
판매 국가
- 공통
- 호주
- 인도
- 캐나다
(지역 內
상세 구분을 위함)
어떤 내용
이 있어야
하는지 상세 안내
Checking data 표준 문장 점검 결과 (매뉴얼 점검 항목은 대상 아님)
비고 란
지역과 판매국가를 이중관리하는 이유는 제품 판매하는 영업 정책에 따름
U.I에 반영되어야 하는 항목
Evidence = 점검 콘텐츠
Evidence = 문장 위치
매뉴얼 점검 툴은 점검결과를 통해 나타나는
신뢰도(유사도), 정답 여부, 정답 입력, 검수자 추가 반영 필요함.